Change Request on IEC 60617-S00044, follow up to C00135

| Type of request: |  | Technical modification |
| --- | --- | --- |
| Proposal: |  | An alternative name "Test terminal, twin stud type” should be added to S00044: Connecting link, closed in order to clarify a use of the symbol. |
| Reason: |  | S00044 is generally used as the symbol for a pair of terminals with a short-circuit bar in the electric power industry, which is called “test terminal.” “Test terminal” is a stud type terminal on a front panel of the distribution and/or the control panel of a power plant and so on. It is inserted to the secondary circuit of an instrument transformer. When relays and meters connected to the secondary circuit of the instrument transformer is going to be calibrated and tested, they are separated from the secondary circuit by removing the short-circuit bar. |
| Drawing: |  |  |
| Description (temporary field) | EN |  |
|  | FR |  |
| Name: | EN | Connecting link, closed |
|  | FR |  |
| Keywords: | EN | Connection devices, test terminals |
|  | FR |  |
| Form: | EN |  |
|  | FR |  |
| Remarks: |  |  |
| Application notes: |  |  |
| Alternative names: |  | Test terminal, twin stud type |
| Alternative forms: |  | S00045 |
| Applied in: |  |  |
| Applies: |  | S00017 |
| Source references: |  |  |
| Published in: |  |  |
| Entered on: |  |  |
| Evaluated on: |  |  |
| Released on: |  |  |
| Rejected on: |  |  |
| Obsolete on: |  |  |
| Proposed by: |  | JNC |
| Replaces: |  |  |
| Replaced by: |  |  |
| Application class: |  | Circuit diagrams, Connection diagrams, Function diagrams, Installation diagrams |
| Function class: |  | X Connecting |
| Shape class: |  | Circles, Depicting shapes |
| Symbol restrictions: |  |  |